## Detectors
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-A BMC | L01D001 | True | 09:46:43A TUE JUN 04, 2019
TROUBL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-A BMC | L01D002 | True | 09:47:18A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-B BMC | L01D003 | True | 10:12:41A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-B BMC | L01D004 | True | 10:13:16A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-C BMC | L01D005 | True | 10:26:38A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-C BMC | L01D006 | True | 10:27:01A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-D BMC | L01D007 | True | 10:34:40A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | PENTHOUSE LOAD CTR-D BMC | L01D008 | True | 10:34:58A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | 3RD FL TELEPHONE RM BMC | L01D009 | True | 10:52:06A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | W-MASS SWITCHGEAR RM BMC FL N-W | L01D010 | True | 02:53:34P WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | W-MASS SWITCHGEAR RM BMC FL N-W | L01D011 | True | 02:53:28P WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | CTR CONTROL CEILING BMC FLOOR | L01D012 | True | 08:50:28A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | CTR CONTROL CEILING BMC FLOOR | L01D013 | True | 08:50:51A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | CTR CONTROL FLOOR BMC FLOOR | L01D014 | True | 08:55:59A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | CTR CONTROL FLOOR BMC FLOOR | L01D015 | True | 08:53:28A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | COMPUTER RM CEILING BMC FLOOR | L01D016 | True | 08:47:46A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | COMPUTER RM CEILING BMC FLOOR | L01D017 | True | 08:45:20A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | COMPUTER RM FLOOR BMC FLOOR | L01D018 | True | 08:51:32A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | COMPUTER RM FLOOR BMC FLOOR | L01D019 | True | 08:57:15A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | COMP RM REGULATOR RM BMC FLOOR | L01D020 | False
NORMAL | SMOKE DUCT-P | ABOVE 2 SUBCEILINGS BMC 1ST MED | L01D021 | False
NORMAL | SMOKE(PHOTO) | ELEVATOR MECH ROOM BMC 1ST FL | L01D022 | False
NORMAL | SMOKE(PHOTO) | MAIN LOBBY ELEVATOR BMC 1ST FL | L01D023 | False
NORMAL | SMOKE(PHOTO) | 2ND FLOOR ELEVATOR BMC 2ND FL | L01D024 | False
NORMAL | SMOKE(PHOTO) | 3RD FLOOR ELEVATOR BMC 3RD FL | L01D025 | False
NORMAL | SMOKE(PHOTO) | PENTHOUSE ELEVATOR BMC 4TH FL | L01D026 | False
NORMAL | SMOKE DUCT-P | AC-21 SUPPLY COL K-1 BMC-MEZZ-SW | L01D028 | True | 09:07:43A WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | AC-21 RETURN COL K-1 BMC-MEZZ-SW | L01D029 | True | 09:09:16A WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | MAILFLOW COL C10 SC P&DC MEZZ | L02D001 | False
NORMAL | SMOKE(PHOTO) | ELEC RM COL C9 P&DC MEZZ | L02D002 | True | 11:47:01A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | ELEC RM COL C8 P&DC MEZZ | L02D003 | True | 11:46:26A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU3 RETURN COL C8 P&DC MEZZ | L02D004 | True | 11:43:55A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU3 SUPPLY COL D8 P&DC MEZZ | L02D005 | True | 11:44:59A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU4 RETURN COL C7 P&DC MEZZ | L02D006 | True | 11:31:08A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU4 SUPPLY COL D7 P&DC MEZZ | L02D007 | True | 11:38:00A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU2 RETURN COL C6 P&DC MEZZ | L02D008 | True | 11:38:35A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU2 RETURN COL D6 P&DC MEZZ | L02D009 | True | 11:42:10A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU1 SUPPLY COL D5 P&DC MEZZ | L02D010 | True | 11:29:46A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AHU1 RETURN COL D5 P&DC MEZZ | L02D011 | True | 11:26:12A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | RTU7 RETURN COL F0.5 P&DC MEZZ | L02D014 | False
NORMAL | SMOKE DUCT-P | RTU 6RETURN COL E0.5 P&DC MEZZ | L02D015 | False
NORMAL | HEAT+ | NDC NORTH BOILER RM NORTH P&DC | L02D021 | True | 01:09:31P TUE JUN 04, 2019
NORMAL | HEAT+ | NDC NORTH BOILER RM SOUTH P&DC | L02D022 | True | 01:10:53P TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | COMPUTER ROOM N104 FSS | L03D001 | False
NORMAL | SMOKE DUCT-P | PH RTU #2 SUPPLY FSS | L03D002 | True | 01:35:57P WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | PH RTU #2 SUPPLY FSS | L03D003 | True | 01:35:46P WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | PH RTU #2 RETURN FSS | L03D004 | True | 01:38:40P WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | AHU-14 RETURN BMC-EAST | L03D048 | False
NORMAL | SMOKE(PHOTO) | ELECTRIC ROOM BMC-EAST | L03D049 | True | 11:23:16A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | BREAK ROOM-WEST SIDE BMC-EAST | L03D050 | True | 11:42:21A WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | AHU-C6 COL V-5.5 CONNECTOR | L03D069 | False
NORMAL | SMOKE DUCT-P | AHU-C7 COL X-2 CONNECTOR | L03D070 | False
NORMAL | SMOKE(PHOTO) | OFFICE COLUMN W-1 CONNECTOR | L03D071 | True | 10:55:40A WED JUN 05, 2019
NORMAL | HEAT(ROR) | MENS ROOM COL W 2 CONNECTOR | L03D072 | True | 11:05:45A WED JUN 05, 2019
NORMAL | HEAT(ROR) | WOMENS RM COL W 4.5 CONNECTOR | L03D073 | True | 11:08:28A WED JUN 05, 2019
NORMAL | HEAT(ROR) | BREAK AREA COL A-1 CONNECTOR | L03D074 | True | 10:59:33A WED JUN 05, 2019
NORMAL | HEAT(ROR) | BREAK AREA E COL A-1 CONNECTOR | L03D075 | True | 10:59:04A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | LOCKER ROOM CONNECTOR | L03D076 | True | 11:09:55A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | BATTERY RM ENTRY BMC-EAST | L03D077 | True | 11:11:22A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | BATTERY RM CEILING BMC-EAST | L03D078 | True | 11:14:05A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | BATTERY RM REAR BMC-EAST | L03D079 | True | 11:14:57A WED JUN 05, 2019
NORMAL | SMOKE(PHOTO) | BATTERY RM CEILING BMC-EAST | L03D080 | True | 11:12:56A WED JUN 05, 2019
NORMAL | SMOKE DUCT-P | BATTERY RM AHU 18 BMC-EAST | L03D081 | False
NORMAL | SMOKE DUCT-P | AC-1 SUPPLY REAR BMC-PENTHOUS | L04D001 | True | 10:00:03A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-1 RETURN REAR BMC-PENTHOUS | L04D002 | True | 10:01:30A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-2 SUPPLY REAR BMC-PENTHOUS | L04D003 | True | 10:03:38A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-2 RETURN REAR BMC-PENTHOUS | L04D004 | True | 10:04:42A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-3 SUPPLY REAR BMC-PENTHOUS | L04D005 | True | 10:05:29A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-3 RETURN REAR BMC-PENTHOUS | L04D006 | True | 10:06:27A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-4 SUPPLY REAR BMC-PENTHOUS | L04D007 | True | 10:08:06A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-4 RETURN REAR BMC-PENTHOUS | L04D008 | True | 10:09:10A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-5 SUPPLY REAR BMC-PENTHOUS | L04D009 | True | 10:09:56A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-5 RETURN REAR BMC-PENTHOUS | L04D010 | True | 10:10:49A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-6 SUPPLY REAR BMC-PENTHOUS | L04D011 | True | 10:11:24A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-6 RETURN REAR BMC-PENTHOUS | L04D012 | True | 10:12:51A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-7 SUPPLY REAR BMC-PENTHOUS | L04D013 | True | 10:13:20A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-7 RETURN REAR BMC-PENTHOUS | L04D014 | True | 10:14:41A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-8 SUPPLY REAR BMC-PENTHOUS | L04D015 | True | 10:17:13A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-8 RETURN REAR BMC-PENTHOUS | L04D016 | True | 10:18:10A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-9 SUPPLY REAR BMC-PENTHOUS | L04D017 | True | 10:20:30A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-9 RETURN REAR BMC-PENTHOUS | L04D018 | True | 10:21:46A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-10 SUPPLY REAR BMC-PENTHOUS | L04D019 | True | 10:23:13A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-10 RETURN REAR BMC-PENTHOUS | L04D020 | True | 10:24:11A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-11 SUPPLY REAR BMC-PENTHOUS | L04D021 | True | 10:24:34A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-11 RETURN REAR BMC-PENTHOUS | L04D022 | True | 10:25:32A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-12 SUPPLY REAR BMC-PENTHOUS | L04D023 | True | 10:25:50A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-12 RETURN REAR BMC-PENTHOUS | L04D024 | True | 10:27:11A TUE JUN 04, 2019
TROUBL | SMOKE DUCT-P | AC-13 SUPPLY REAR BMC-PENTHOUS | L04D025 | False
NORMAL | SMOKE DUCT-P | AC-13 RETURN REAR BMC-PENTHOUS | L04D026 | True | 10:30:17A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-14 SUPPLY REAR BMC-PENTHOUS | L04D027 | True | 10:31:21A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-14 RETURN REAR BMC-PENTHOUS | L04D028 | True | 10:32:08A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-15 SUPPLY REAR BMC-PENTHOUS | L04D029 | True | 10:32:54A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-15 RETURN REAR BMC-PENTHOUS | L04D030 | True | 10:33:46A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-16 SUPPLY REAR BMC-PENTHOUS | L04D031 | True | 10:33:52A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-16 RETURN REAR BMC-PENTHOUS | L04D032 | True | 10:36:00A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-17 SUPPLY REAR BMC-PENTHOUS | L04D033 | True | 10:35:54A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-17 RETURN REAR BMC-PENTHOUS | L04D034 | True | 10:36:58A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-18 SUPPLY REAR BMC-PENTHOUS | L04D035 | True | 10:39:41A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-18 RETURN REAR BMC-PENTHOUS | L04D036 | True | 10:37:33A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-19 SUPPLY REAR BMC-PENTHOUS | L04D037 | True | 10:39:12A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-19 RETURN REAR BMC-PENTHOUS | L04D038 | True | 10:40:16A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-20 SUPPLY BY BATH BMC-PENTHOUS | L04D039 | True | 10:15:00A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AC-20 RETURN BY BATH BMC-PENTHOUS | L04D040 | True | 10:15:52A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AH 101 SUPPLY REAR BMC-PENTHOUS | L04D041 | True | 09:53:34A TUE JUN 04, 2019
NORMAL | SMOKE DUCT-P | AH 101 RETURN REAR BMC-PENTHOUS | L04D042 | True | 09:55:37A TUE JUN 04, 2019
NORMAL | SMOKE(PHOTO) | TEST SMOKE THIS ROOM | L04D043 | False

## Modules
NORMAL | PULL STATION | LOAD CTR A NORTHWEST BMC-PENTHOUS | L01M001 | True | 09:48:20A TUE JUN 04, 2019
NORMAL | TAMPER | ZONE 2 BEHIND AHU1 BMC-PENTHOUS | L01M002 | False
NORMAL | MONITOR | WATERFLOW ZONE 2 BMC-PENTHOUS | L01M003 | False
NORMAL | PULL STATION | ACROSS AHU1 ON COL BMC-PENTHOUS | L01M004 | True | 09:57:23A TUE JUN 04, 2019
NORMAL | PULL STATION | LOAD CTR B ON COL-F7 BMC-PENTHOUS | L01M005 | True | 10:15:47A TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW ZONE 10-F BMC-PENTHOUS | L01M006 | False
NORMAL | TAMPER | ZONE 10-F BY LCS-C BMC-PENTHOUS | L01M007 | False
NORMAL | PULL STATION | LCS-C COL F-10 BMC-PENTHOUS | L01M008 | True | 10:29:21A TUE JUN 04, 2019
NORMAL | PULL STATION | LCS-D COL D-13 BMC-PENTHOUS | L01M009 | True | 10:35:19A TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW ZONE 10-A BMC-PENTHOUS | L01M010 | False
NORMAL | TAMPER | COL 13 BY ROOF EXIT BMC-PENTHOUS | L01M011 | False
NORMAL | PULL STATION | BY ELEV & STAIRS BMC-PENTHOUS | L01M012 | True | 10:41:09A TUE JUN 04, 2019
NORMAL | PULL STATION | BY EXIT TO P&DC ROOF BMC-3RD FL | L01M013 | True | 10:56:52A TUE JUN 04, 2019
DISABL | PULL STATION | LOBBY BY ELEV LEFT BMC-3RD FL | L01M014 | True | 10:44:45A TUE JUN 04, 2019
NORMAL | PULL STATION | BY STAIRS TO PENT W BMC-3RD FL | L01M015 | True | 10:55:25A TUE JUN 04, 2019
NORMAL | PULL STATION | BY STAIRS SW DOOR BMC-3RD FL | L01M016 | True | 10:53:56A TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW RM 353 BMC-3RD FL | L01M017 | False
NORMAL | MONITOR | WATERFLOW RM 353 BMC-3RD FL | L01M018 | False
NORMAL | MONITOR | WATERFLOW RM 353 BMC-3RD FL | L01M019 | False
NORMAL | MONITOR | WATERFLOW RM 353 BMC-3RD FL | L01M020 | False
NORMAL | TAMPER | TAMPER ROOM 333 BMC-3RD FL | L01M021 | False
NORMAL | MONITOR | WATERFLOW RM 333 BMC-3RD FL | L01M022 | False
NORMAL | MONITOR | WATERFLOW RM 333 BMC-3RD FL | L01M023 | False
NORMAL | MONITOR | WATERFLOW RM 333 BMC-3RD FL | L01M024 | False
NORMAL | MONITOR | WATERHEATER RM309 WF BMC-3RD FL | L01M025 | False
NORMAL | TAMPER | TAMPER RM 309 BMC-3RD FL | L01M026 | False
NORMAL | PULL STATION | NORTH WALL BY RM 246 BMC-2ND FL | L01M027 | True | 11:01:28A TUE JUN 04, 2019
NORMAL | PULL STATION | BY ELEV & STAIRS BMC-2ND FL | L01M028 | True | 11:09:03A TUE JUN 04, 2019
NORMAL | PULL STATION | BY STAIRS TO PENT W BMC-2ND FL | L01M029 | True | 11:11:51A TUE JUN 04, 2019
NORMAL | PULL STATION | SW DOOR BY RM 212 BMC-2ND FL | L01M030 | True | 11:10:28A TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW RM 207 BMC-2ND FL | L01M031 | False
NORMAL | TAMPER | ROOM 207 BY SAFETY BMC-2ND FL | L01M032 | False
NORMAL | PULL STATION | NE MENS ROOM BMC-1ST FL | L01M033 | True | 03:37:54P TUE JUN 04, 2019
NORMAL | PULL STATION | NE MEN LOCKER RM BMC-1ST FL | L01M034 | True | 03:38:08P TUE JUN 04, 2019
NORMAL | PULL STATION | ENTRY TO BMC BMC-1ST FL | L01M035 | True | 04:06:39P TUE JUN 04, 2019
NORMAL | PULL STATION | NE MENS LOCKER RM BMC-1ST FL | L01M036 | True | 03:57:54P TUE JUN 04, 2019
NORMAL | PULL STATION | REC AREA BY UNION BMC-1ST FL | L01M037 | True | 02:35:26P WED JUN 05, 2019
NORMAL | PULL STATION | REC AREA BY UNION BMC-1ST FL | L01M038 | True | 02:22:16P WED JUN 05, 2019
NORMAL | PULL STATION | WOMENS LOCKER REAR BMC-1ST FL | L01M039 | True | 02:00:29P WED JUN 05, 2019
NORMAL | PULL STATION | MAIN EXIT BY GUARD BMC-1ST FL | L01M041 | True | 01:33:16P WED JUN 05, 2019
NORMAL | PULL STATION | MAIN ENTRY NORTH BMC-1ST FL | L01M042 | True | 01:33:30P WED JUN 05, 2019
DISABL | CONTROL | COLUMN E4 BY FLOOR BMC-FLOOR | L01M043 | False
DISABL | RELAY | COLUMN E4 BY FLOOR BMC-FLOOR | L01M044 | False
DISABL | MONITOR | WATERFLOW-ZONE 10AA BMC-FLOOR | L01M045 | False
NORMAL | PULL STATION | COL A-13 NORTH ISLE BMC-FLOOR | L01M046 | True | 02:35:37P TUE JUN 04, 2019
DISABL | MONITOR | WATERFLOW ZONE 10-A BMC-FLOOR | L01M047 | False
NORMAL | TAMPER | PIV ZONE 10A-COL A11 BMC-FLOOR | L01M048 | False
NORMAL | PULL STATION | COL A-9 BY DOOR B18 BMC-FLOOR | L01M049 | True | 02:38:38P TUE JUN 04, 2019
DISABL | TAMPER | PIV ZONE 6A DOOR 230 BMC-FLOOR | L01M050 | False
DISABL | MONITOR | WATERFLOW ZONE 6A BMC-FLOOR | L01M051 | False
NORMAL | PULL STATION | DOCK DOOR 233 BMC-FLOOR | L01M052 | True | 02:40:15P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR B-20 COL A-3 BMC-FLOOR | L01M053 | True | 02:41:03P TUE JUN 04, 2019
NORMAL | TAMPER | PIV ZONE 2 N. RAMP BMC-FLOOR | L01M054 | False
DISABL | MONITOR | WATERFLOW ZONE 2A BMC-FLOOR | L01M055 | False
DISABL | MONITOR | WF DRY SYS ZONE 1A BMC-FLOOR | L01M056 | False
DISABL | MONITOR | WF WET SYS ZONE 1A BMC-FLOOR | L01M057 | False
DISABL | TAMPER | Z 1A NW LOW PRESSURE BMC-FLOOR | L01M058 | False
DISABL | TAMPER | ZONE 1A NW COL A1 BMC-FLOOR | L01M059 | True | 09:03:24A TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR B-23 TO W TRUCK BMC-FLOOR | L01M060 | True | 02:42:17P TUE JUN 04, 2019
NORMAL | PULL STATION | BY DOCK DOORS 4&5 BMC-FLOOR | L01M061 | True | 02:44:19P TUE JUN 04, 2019
DISABL | TAMPER | PIV WMECO SWITCH RM BMC-FLOOR | L01M062 | False
NORMAL | PULL STATION | COL E-4 UNDER PSM-3E BMC-FLOOR | L01M063 | True | 04:02:20P TUE JUN 04, 2019
NORMAL | PULL STATION | COL D-7 UNDER PSM-3 BMC-FLOOR | L01M064 | True | 04:00:55P TUE JUN 04, 2019
NORMAL | PULL STATION | COL D-10 UNDER PSM-3 BMC-FLOOR | L01M065 | True | 03:59:57P TUE JUN 04, 2019
NORMAL | PULL STATION | COL E-14 MENS LOCK BMC-FLOOR | L01M066 | True | 03:57:32P TUE JUN 04, 2019
NORMAL | TAMPER | ZONE 10F BY DOOR 71 BMC-FLOOR SE | L01M067 | False
NORMAL | TAMPER | ZONE 15H DOOR 71 BMC-FLOOR | L01M068 | False
NORMAL | MONITOR | WATERFLOW ZONE 15H BMC-FLOOR | L01M069 | False
NORMAL | PULL STATION | EXIT B-35 SW TRUCK BMC-FLOOR | L01M070 | True | 08:40:41A THU JUN 06, 2019
NORMAL | PULL STATION | DOOR B-34 BY DOOR 73 BMC-FLOOR | L01M071 | True | 03:55:22P TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW ZONE 10F BMC-FLOOR | L01M072 | False
NORMAL | TAMPER | PIV ZONE 10F DOOR 71 BMC-FLOOR | L01M073 | False
NORMAL | PULL STATION | DOOR B-33 BY DOOR 57 BMC-FLOOR | L01M074 | True | 03:49:58P TUE JUN 04, 2019
NORMAL | PULL STATION | COL H10 NW ISLE BMC-FLOOR | L01M075 | True | 03:41:58P TUE JUN 04, 2019
NORMAL | PULL STATION | 3RD LEVEL SACK SHAKE BMC-FLOOR | L01M076 | True | 03:09:46P WED JUN 05, 2019
NORMAL | MONITOR | WATERFLOW ZONE 6F BMC-FLOOR | L01M077 | False
DISABL | TAMPER | PIV BY DOORS 55&56 BMC-FLOOR | L01M078 | False
NORMAL | PULL STATION | EW ISLE BY ET/SHOP BMC-FLOOR | L01M079 | True | 03:43:47P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR B-32 BY DOOR 41 BMC-FLOOR | L01M080 | True | 03:48:01P TUE JUN 04, 2019
DISABL | MONITOR | WATERFLOW ZONE 2-F BMC-FLOOR | L01M081 | False
DISABL | TAMPER | PIV BY DOORS 39&40 BMC-FLOOR | L01M082 | True | 09:09:59A TUE JUN 04, 2019
NORMAL | PULL STATION | COL H4 WEST PRIMARY BMC-FLOOR | L01M083 | True | 03:44:49P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR B-31 BY DOOR 26 BMC-FLOOR | L01M084 | True | 02:47:35P TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW ZONE 1-D BMC-FLOOR | L01M085 | False
NORMAL | TAMPER | PIV L1 BY DOOR 52 BMC-FLOOR | L01M086 | False
NORMAL | PULL STATION | DOOR B-26 SW CORNER BMC-FLOOR | L01M087 | True | 02:46:45P TUE JUN 04, 2019
NORMAL | PULL STATION | BETWEEN DOORS 18&19 BMC-FLOOR | L01M088 | True | 02:45:46P TUE JUN 04, 2019
NORMAL | PULL STATION | BY CENTRAL CONTROL BMC-FLOOR | L01M089 | True | 08:49:38A WED JUN 05, 2019
NORMAL | PULL STATION | BY COMPUTER ROOM BMC-FLOOR | L01M090 | True | 08:48:13A WED JUN 05, 2019
DISABL | STROBE CKT | TRIP FCPS TO FSS H/S ALARM RM | L01M092 | False
NORMAL | PULL STATION | STAIR BY DOOR 78 BMC-FLOOR | L01M093 | True | 09:21:24A WED JUN 05, 2019
DISABL | MONITOR | WATERFLOW ZONE 2-F BMC-PENTHOUS | L01M094 | False
NORMAL | TAMPER | ZONE 2-F ABOVE MCC2B BMC-PENTHOUS | L01M095 | False
NORMAL | MONITOR | TELE ROOM THERMOSTAT BMC-3RD FL | L01M096 | False
OFF | RELAY | ELEV RECALL TO 1ST BMC-LOBBY | L01M097 | False
OFF | RELAY | ELEV RECALL TO 2ND BMC-LOBBY | L01M098 | False
NORMAL | MONITOR | HORN ACTIVATE SWITCH BMC-1ST FL | L01M099 | False
DISABL | RELAY | ZONE 10 A BMC-BEACON | L01M101 | False
DISABL | RELAY | ZONE 6 A BMC-BEACON | L01M102 | False
DISABL | RELAY | ZONE 2 A BMC-BEACON | L01M103 | False
DISABL | RELAY | ZONE 1 A BMC-BEACON | L01M104 | False
DISABL | RELAY | WEST BY DOORS 8 & 9 BMC-BEACON | L01M105 | False
DISABL | RELAY | ZONE 1 D BMC-BEACON | L01M106 | False
DISABL | RELAY | ZONE 12 F BMC-BEACON | L01M107 | False
DISABL | RELAY | ZONE 6 F BMC-BEACON | L01M108 | False
DISABL | RELAY | ZONE 10 F BMC-BEACON | L01M109 | False
NORMAL | PULL STATION | COL G20 BMC-FLOOR | L01M111 | True | 09:35:10A WED JUN 05, 2019
DISABL | RELAY | BMC & GMF/P &DC RADIOBOX TRP | L01M112 | False
DISABL | RELAY | BMC-EAST / MPA RADIOBOX TRP | L01M113 | False
DISABL | RELAY | PUMP HOUSE RADIOBOX TRP | L01M114 | False
NORMAL | POWER MONITR | MAIN POWER SUPPLY GENERAL | L01M155 | False
NORMAL | POWER MONITR | MAIN POWER SUPPLY AC FAIL | L01M156 | False
NORMAL | POWER MONITR | MAIN POWER SUPPLY BATTERY | L01M157 | False
DISABL | POWER MONITR | MAIN POWER SUPPLY EARTH FAULT | L01M158 | False
NORMAL | PULL STATION | DOOR G-12 BY DOOR201 P & DC DOCKS | L02M001 | True | 01:59:33P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR G-13 BY DOOR206 P & DC DOCKS | L02M002 | True | 01:57:38P TUE JUN 04, 2019
NORMAL | PULL STATION | VESTIBULE BY DOOR204 P & DC DOCKS | L02M003 | True | 01:15:07P TUE JUN 04, 2019
NORMAL | PULL STATION | ACROSS FROM DOOR 209 P & DC DOCKS | L02M004 | True | 01:56:59P TUE JUN 04, 2019
NORMAL | PULL STATION | ACROSS COL C5 P & DC DOCKS | L02M005 | True | 01:14:26P TUE JUN 04, 2019
NORMAL | PULL STATION | ACROSS COL D6 P & DC DOCKS | L02M006 | True | 01:13:20P TUE JUN 04, 2019
NORMAL | PULL STATION | TIMECLOCK BREAK AREA P & DC DOCKS | L02M007 | True | 01:22:10P TUE JUN 04, 2019
NORMAL | PULL STATION | COL D3 STANDUP DESK P & DC DOCKS | L02M008 | True | 01:35:03P TUE JUN 04, 2019
NORMAL | PULL STATION | MAIN ISLE COL F3 P & DC DOCKS | L02M009 | True | 01:24:05P TUE JUN 04, 2019
NORMAL | PULL STATION | BY WOMEN RM COL G1 P & DC DOCKS | L02M010 | True | 01:21:20P TUE JUN 04, 2019
NORMAL | PULL STATION | OFFICE MEZZ COL H1 P & DC DOCKS | L02M011 | True | 01:20:43P TUE JUN 04, 2019
NORMAL | PULL STATION | COLUNM F-5 P & DC DOCKS | L02M012 | True | 01:36:15P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR G-4 COLUMN J4 P & DC DOCKS | L02M013 | True | 01:37:11P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR G-14 BY DOOR214 P & DC DOCKS | L02M014 | True | 01:55:46P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR BY DOORS219&220 P & DC DOCKS | L02M015 | True | 01:55:04P TUE JUN 04, 2019
NORMAL | PULL STATION | ACROSS COL D8 P & DC DOCKS | L02M016 | True | 01:12:42P TUE JUN 04, 2019
NORMAL | PULL STATION | DOOR G-15 BY DOOR224 P & DC DOCKS | L02M017 | True | 01:54:13P TUE JUN 04, 2019
NORMAL | PULL STATION | COMPACTOR DOOR P & DC DOCKS | L02M018 | True | 01:53:16P TUE JUN 04, 2019
NORMAL | PULL STATION | BY C11 PASSAGEWAY P & DC DOCKS | L02M019 | True | 01:52:19P TUE JUN 04, 2019
NORMAL | PULL STATION | ACROSS COL D10 P & DC DOCKS | L02M020 | True | 01:11:47P TUE JUN 04, 2019
NORMAL | PULL STATION | BY C11 PASSAGEWAY R P & DC DOCKS | L02M021 | True | 01:08:52P TUE JUN 04, 2019
NORMAL | PULL STATION | COL C11 DOCK AREA P & DC DOCKS | L02M022 | True | 01:04:30P TUE JUN 04, 2019
NORMAL | PULL STATION | COL F8 WORK ROOM P & DC DOCKS | L02M023 | True | 01:41:26P TUE JUN 04, 2019
NORMAL | PULL STATION | COL G7 WORK ROOM P & DC DOCKS | L02M024 | True | 01:38:51P TUE JUN 04, 2019
NORMAL | PULL STATION | EAST WALL BY G3 P & DC DOCKS | L02M025 | True | 01:38:11P TUE JUN 04, 2019
NORMAL | PULL STATION | EAST WALL BY G2 P & DC DOCKS | L02M026 | True | 01:42:47P TUE JUN 04, 2019
NORMAL | PULL STATION | COL F10 WORK ROOM P & DC DOCKS | L02M027 | True | 01:44:43P TUE JUN 04, 2019
NORMAL | PULL STATION | SOUTH WALL COL G13 P & DC DOCKS | L02M028 | True | 01:46:36P TUE JUN 04, 2019
NORMAL | PULL STATION | CAF? EAST J11 P & DC DOCKS | L02M029 | True | 01:43:35P TUE JUN 04, 2019
NORMAL | PULL STATION | OFFICE AREA COL H10 P & DC DOCKS | L02M030 | True | 01:54:37P WED JUN 05, 2019
NORMAL | PULL STATION | NDC NORTH BOILER RM NORTH P&DC | L02M031 | True | 01:09:59P TUE JUN 04, 2019
NORMAL | PULL STATION | NDC NORTH BOILER RM SOUTH P&DC | L02M032 | True | 01:10:13P TUE JUN 04, 2019
NORMAL | PULL STATION | OUTSIDE COMPUTER RM P & DC M EZZ | L02M033 | True | 01:16:52P TUE JUN 04, 2019
NORMAL | PULL STATION | TOUR SUPV OFFFICE P & DC MEZZ | L02M034 | True | 01:18:54P TUE JUN 04, 2019
NORMAL | PULL STATION | IN STAIR BY G-5 P & DC MEZZ | L02M035 | True | 01:20:02P TUE JUN 04, 2019
NORMAL | PULL STATION | ACROSS AHU G-1 P & DC MEZZ | L02M036 | True | 11:25:12A TUE JUN 04, 2019
NORMAL | PULL STATION | MAIL FLOW CON RM P & DC MEZZ | L02M037 | True | 11:48:48A TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW ZONE 1&3 P & DC FLOOR | L02M038 | False
NORMAL | MONITOR | WATERFLOW ZONE 1&3 P & DC FLOOR | L02M039 | False
NORMAL | TAMPER | ZONE 1&3 WEST STAIR P & DC FLOOR | L02M040 | False
NORMAL | MONITOR | WATERFLOW ZONE 10AA P & DC FLOOR | L02M041 | False
NORMAL | MONITOR | WATERFLOW ZONE 2&4 P & DC FLOOR | L02M042 | False
NORMAL | TAMPER | ZONE 10AA BREAK AREA P & DC FLOOR | L02M043 | False
NORMAL | TAMPER | PIV COL E3 E/W ISLE P & DC FLOOR | L02M044 | False
NORMAL | TAMPER | PIV COL E3 E/W ISLE P & DC FLOOR | L02M045 | False
DISABL | TAMPER | J-9 WATER FLOW P & DC FLOOR | L02M046 | True | 12:20:19P TUE JUN 04, 2019
NORMAL | MONITOR | WATERFLOW ZONE 5&7 P & DC FLOOR | L02M047 | False
NORMAL | TAMPER | PIV COL J9 EAST WALL P & DC FLOOR | L02M048 | False
DISABL | TAMPER | COL J9 EAST WALL P & DC FLOOR | L02M049 | False
NORMAL | TRACK SUPERV | LOW-AIR DRY SYSTEM P&DC FLOOR | L02M052 | False
DISABL | HORN CIRCUIT | P&DC CIRCUIT 1 FIRE CONT RM | L02M080 | False
DISABL | HORN CIRCUIT | P&DC CIRCUIT 2 FIRE CONT RM | L02M081 | False
DISABL | HORN CIRCUIT | BMC CIRCUIT 1 FIRE CONT RM | L02M082 | False
DISABL | HORN CIRCUIT | BMC CIRCUIT 2 FIRE CONT RM | L02M083 | False
DISABL | HORN CIRCUIT | BMC CIRCUIT 3 FIRE CONT RM | L02M084 | False
DISABL | RELAY | SEC DOOR LOCKS FIRE CONT RM | L02M085 | False
DISABL | HORN CIRCUIT | PRESIGNAL BELLS FIRE CONT RM | L02M087 | False
DISABL | RELAY | 6 MIN DELAY TIMER FIRE CONT RM | L02M088 | False
DISABL | SMOKE CONVEN | SMOKE-6 MIN DELAY FIRE CONT RM | L02M089 | False
NORMAL | TROUBLE MON | SYSTEM TROUBLE FIRE CONT RM | L02M090 | False
DISABL | RELAY | MECHANICAL TRIP FIRE CONT RM | L02M091 | False
DISABL | HORN CIRCUIT | P&DC CIRCUIT 3 FIRE CONT RM | L02M092 | False
DISABL | HORN CIRCUIT | CONNECTOR BLDG CIR1 FIRE CONT RM | L02M093 | False
DISABL | RELAY | SEC DOOR LOCKS FIRE CONT RM | L02M095 | False
DISABL | TROUBLE MON | FCPS-FIRE CONTROL RM BOTTOM LEFT | L02M096 | False
DISABL | HORN CIRCUIT | DIESEL PUMP HOUSE OUT BUILDING | L03M001 | False
NORMAL | TRACK SUPERV | CARPENTER SHOP OUT BUILDING | L03M002 | True | 10:33:25A THU JUN 06, 2019
NORMAL | TRACK SUPERV | EVS BUILDING OUT BUILDING | L03M003 | True | 10:17:04A THU JUN 06, 2019
NORMAL | PULL STATION | BY EXIT DOOR FSS-SAT MAIT | L03M004 | True | 10:24:18A WED JUN 05, 2019
NORMAL | PULL STATION | EGRESS CORRIDOR FSS-COR N113 | L03M005 | True | 02:08:33P WED JUN 05, 2019
NORMAL | TRACK SUPERV | VMF BUILDING OUT BUILDING | L03M006 | False
NORMAL | PULL STATION | WORK RM VESTIBULE FSS-RM N111 | L03M007 | True | 11:58:45A WED JUN 05, 2019
NORMAL | PULL STATION | WORK RM VESTIBULE FSS-RM N111 | L03M008 | True | 11:58:54A WED JUN 05, 2019
NORMAL | PULL STATION | WORK RM VESTIBULE FSS-RM N111 | L03M009 | True | 11:58:40A WED JUN 05, 2019
NORMAL | MONITOR | AHU-13 SUPPLY BMC-EAST | L03M010 | False
NORMAL | MONITOR | AHU-13 RETURN BMC-EAST | L03M011 | False
NORMAL | MONITOR | AHU-14 SUPPLY BMC-EAST | L03M012 | False
NORMAL | PULL STATION | BY EXIT DOOR FSS-SAT MAIT | L03M013 | True | 10:24:13A WED JUN 05, 2019
NORMAL | MONITOR | AHU-15 SUPPLY BMC-EAST | L03M014 | False
NORMAL | MONITOR | AHU-15 RETURN BMC-EAST | L03M015 | False
NORMAL | MONITOR | AHU-17 SUPPLY BMC-EAST | L03M016 | False
NORMAL | MONITOR | AHU-17 RETURN BMC-EAST | L03M017 | False
NORMAL | MONITOR | AHU-16 SUPPLY BMC-EAST | L03M018 | False
DISABL | MONITOR | AHU-16 RETURN BMC-EAST | L03M019 | False
NORMAL | TAMPER | ZONE 9 BOILER RM BMC-EAST | L03M020 | False
NORMAL | MONITOR | WATERFLOW ZONE 9 BMC-EAST | L03M021 | False
NORMAL | TAMPER | ZONE 8 BOILER RM BMC-EAST | L03M022 | False
NORMAL | MONITOR | WATERFLOW ZONE 8 BMC-EAST | L03M023 | False
NORMAL | PULL STATION | BREAK ROOM BMC-EAST | L03M024 | True | 11:42:18A WED JUN 05, 2019
NORMAL | PULL STATION | COL D2 BY CUSTODIAN BMC-EAST | L03M025 | True | 11:20:15A WED JUN 05, 2019
NORMAL | PULL STATION | E62 BY ELEC RM BMC-EAST | L03M027 | True | 11:22:34A WED JUN 05, 2019
NORMAL | PULL STATION | E63 BY DOORS 332&333 BMC-EAST | L03M029 | True | 11:35:55A WED JUN 05, 2019
NORMAL | PULL STATION | EGRESS CORRIDOR FSS-COR N113 | L03M030 | True | 01:41:39P WED JUN 05, 2019
DISABL | RELAY | JOHNSON CONTROL MOD BMC-EAST | L03M031 | False
DISABL | HORN CIRCUIT | MOD IN ELEC RM BMC-EAST | L03M032 | False
DISABL | RELAY | SHUNT-TRIP IN ELEC BMC-EAST | L03M035 | False
DISABL | HORN CIRCUIT | ALARM PANEL IN ELEC BMC-EAST | L03M036 | False
NORMAL | TROUBLE MON | ALARM PANEL BCM-E BMC-EAST | L03M037 | False
NORMAL | PULL STATION | BATTERY ROOM BMC-EAST | L03M038 | True | 11:10:40A WED JUN 05, 2019
DISABL | RELAY | AHU18 ELEC PANEL BMC-EAST | L03M039 | False
NORMAL | MONITOR | PRE-ACTION SYS FSS ENTRY AREA | L03M040 | False
NORMAL | TAMPER | PRE-ACTION SYSTEM ENTRY AREA | L03M041 | False
NORMAL | MONITOR | PRE-ACTION SYS FSS WATERFLOW | L03M042 | False
DISABL | RELAY | REVOLVING DOOR REL TURNSTILE | L03M043 | False
DISABL | RELAY | REVOLVING DOOR REL TURNSTILE | L03M044 | False
DISABL | RELAY | REVOLVING DOOR REL TURNSTILE | L03M045 | False
NORMAL | TAMPER | PIV FSS | L03M049 | False
NORMAL | PULL STATION | E53 BY DOCK DOOR 401 CONNECTOR | L03M050 | False
NORMAL | PULL STATION | E61 BOILER ROOM CONNECTOR | L03M053 | True | 03:33:43P WED JUN 05, 2019
NORMAL | PULL STATION | COLUMNS A4&X4 CONNECTOR | L03M054 | True | 10:42:32A WED JUN 05, 2019
NORMAL | PULL STATION | D2 BY BATTERY RM CONNECTOR | L03M055 | True | 11:19:27A WED JUN 05, 2019
NORMAL | PULL STATION | E57 COLUMN V2 CONNECTOR | L03M056 | True | 10:38:45A WED JUN 05, 2019
NORMAL | PULL STATION | E56 COLUMN V8 CONNECTOR | L03M057 | True | 10:27:08A WED JUN 05, 2019
DISABL | RELAY | ROLL UP DOOR EJECTOR CONNECTOR | L03M059 | False
DISABL | RELAY | ROLL UP DOOR PWU CONNECTOR | L03M061 | False
NORMAL | TAMPER | PIV BREAK ROOM CONNECTOR | L03M062 | False
NORMAL | MONITOR | WATERFLOW BREAKROOM CONNECTOR | L03M063 | False
NORMAL | TAMPER | PIV COL V2 CONNECTOR | L03M067 | False
NORMAL | TAMPER | PIV COL W2 CONNECTOR | L03M068 | False
NORMAL | PULL STATION | DOOR TO OFFICE VEST N101 | L03M071 | True | 01:52:52P WED JUN 05, 2019
NORMAL | PULL STATION | DOOR MAIN EXIT VEST N101 | L03M072 | True | 01:52:53P WED JUN 05, 2019
NORMAL | PULL STATION | DOOR MAIN EXIT VEST N101 | L03M073 | True | 01:53:10P WED JUN 05, 2019
NORMAL | PULL STATION | DOOR MAIN EXIT VEST N101 | L03M074 | True | 01:53:10P WED JUN 05, 2019
NORMAL | PULL STATION | EMPLOYEE LUNCH N108 | L03M075 | True | 01:34:22P WED JUN 05, 2019
NORMAL | PULL STATION | EMPLOYEE LUNCH N108 | L03M076 | True | 01:34:40P WED JUN 05, 2019
DISABL | TRACK SUPERV | PRE-ACTION SYS TROUB ENTRY AREA | L03M077 | False
NORMAL | PULL STATION | EMPLOYEE LUNCH N107 BY EM EXIT | L03M078 | True | 01:35:16P WED JUN 05, 2019
NORMAL | PULL STATION | OUTSIDE BREAK AREA ENTRY AREA | L03M079 | True | 01:35:33P WED JUN 05, 2019
OFF | RELAY | PH RTU-#2 SHUTDOWN ENTRY AREA | L03M080 | False
NORMAL | MONITOR | KITCHEN ANSUL SYS | L03M081 | False
DISABL | RELAY | KITCHEN EQUIP SHUTDOWN | L03M082 | False
DISABL | RELAY | KITCHEN EQUIP SHUTDOWN | L03M083 | False
NORMAL | PULL STATION | KITCHEN REAR SEVICE | L03M084 | True | 01:47:04P WED JUN 05, 2019
NORMAL | PULL STATION | BUILDING GROUNDS RM N109 | L03M085 | True | 01:49:24P WED JUN 05, 2019
NORMAL | MONITOR | WATERFLOW CAFETERIA | L03M086 | False
NORMAL | TRACK SUPERV | PRESSURE SWITCH ENTRY AREA | L03M087 | False
NORMAL | TAMPER | TAMPER ENTRY AREA | L03M088 | False
NORMAL | PULL STATION | GUARD SHACK PAGE BLVD | L03M090 | False
NORMAL | TAMPER | PIV OLD RISER 2 COL V12 | L03M091 | False
NORMAL | TAMPER | PIV MAIN FIRE LOOP COL V12 | L03M092 | False
NORMAL | TRACK SUPERV | PRES SW OLD RISER 2 COL V12 | L03M093 | False
NORMAL | MONITOR | FLOW OLD RISER 2 CAF? | L03M094 | False
NORMAL | TAMPER | MAIN OLD RISER 2 COL V12 | L03M095 | False
DISABL | RELAY | SMOKE DAMPER CAF? SHUTDOWN | L03M096 | False
NORMAL | LATCH SUPERV | HEAT DETECTOR PUMPHOUSE | L03M101 | False
NORMAL | LATCH SUPERV | P I V PUMPHOUSE | L03M102 | False
NORMAL | LATCH SUPERV | WATER FLOW PUMPHOUSE | L03M103 | False
NORMAL | LATCH SUPERV | PULL STATION PUMPHOUSE | L03M104 | True | 10:55:58A THU JUN 06, 2019
NORMAL | LATCH SUPERV | DIESEL PUMP RUNNING PUMPHOUSE | L03M105 | False
ACTIVE | LATCH SUPERV | DIESEL CONTROLLER PUMPHOUSE | L03M106 | True | 12:30:57P WED JUN 05, 2019
NORMAL | LATCH SUPERV | JOCKEY POWER LOSS PUMPHOUSE | L03M107 | False
NORMAL | LATCH SUPERV | JOCKEY OVERLOAD PUMPHOUSE | L03M108 | False
NORMAL | LATCH SUPERV | SPARE PUMPHOUSE | L03M109 | False
DISABL | LATCH SUPERV | SPARE PUMPHOUSE | L03M110 | False
OFF | RELAY | AC-9 SHUTDOWN | L04M018 | False